COLPLY BASE 410

COLPLY BASE 410

flood coat and gravel

SPECIFICATIONS

THESE MASTER SPECIFICATIONS CONTAIN ALL SPECIFICATIONS FOR EACH SPECIFIC SOPREMA ROOFING MEMBRANE SYSTEM.

THE EDITOR SHOULD CONTACT A SOPREMA REPRESENTATIVE TO GET ASSISTANCE FOR THE ADAPTATION OR COMPLETION OF SPECIFICATIONS ACCORDING TO THE PARTICULAR CONDITIONS RELATED TO EACH PROJECT.

IMPORTANT: PLEASE BE SURE TO READ THE POLICY STATEMENT IN THE IMPORTANT NOTICES SECTION IN THE FIRST PAGES OF THE SOPREMA RING BINDER.

FOR A COMPLETE DESCRIPTION OF PRODUCTS AND APPLICABLE STANDARDS, PLEASE REFER TO THE TECHNICAL DATA SHEETS ON OUR WEBSITE AT WWW.SOPREMA.CA.

THE ELECTRONIC VERSION OF OUR SPECIFICATIONS IS ALSO AVAILABLE ON SOPREMA’S WEBSITE.

# General

## REFERENCE STANDARD[S]

NOTE TO THE SPECIFIER: The designer of the waterproofing system should investigate with the client which requirements apply to a particular project. Applicable building regulations must be followed. Consult provincial roofing associations, since they could have special requirements, particularly if they offer warranties.

NOTE TO THE SPECIFIER: The National Building Code requires that all roofs, except when permitted (tents, inflatable structures, certain small “assembly occupancy” buildings), must be either Class A, B, or C, as determined in accordance with CAN/ULC-S107-03 “Standard Methods of Fire Tests of Roof Coverings.”

#### [Submit a report, issued by a certified materials testing laboratory, attesting that the specified roofing system was tested in accordance with CSA A123.21-10, Standard test method for the dynamic wind uplift resistance of membrane-roofing systems. Test results shall demonstrate that the roofing system provides a Dynamic Uplift Resistance (DUR) of [   ] kPa for the field surface of the roof, [   ] kPa for the edges of the roof, and [   ] kPa for the corners of the roof.]

#### [Submit a report showing that the specified roofing system has been tested for Wind Uplift Resistance in accordance with FM 4470 Standard. The test results shall demonstrate that the roofing system provides a resistance of [   ] psf for the field surface of the roof. Edges and corners must be installed according to the requirements listed in FM PLPDS 1-29.]

#### [Membranes must meet or exceed requirements of CGSB 37.56–M (9th Draft), Membrane, Modified, Bituminous, Prefabricated, and Reinforced for Roofing.]

#### [Membranes must meet or exceed requirements of ASTM D 6162, Standard Specification for Styrene Butadiene Styrene (SBS) Modified Bituminous Sheet Materials Using a Combination of Polyester and Glass Fibre Reinforcements.]

#### [Membranes must meet or exceed requirements of ASTM D 6163, Standard Specification for Styrene Butadiene Styrene (SBS) Modified Bituminous Sheet Materials Using Glass Fibre Reinforcements.]

#### [Membranes must meet or exceed requirements of ASTM D 6164, Standard Specification for Styrene Butadiene Styrene (SBS) Modified Bituminous Sheet Materials Using Polyester Reinforcements.]

#### [Mineral wool roof insulation boards must meet or exceed requirements of ASTM C726, Standard Specification for Mineral Wool Roof Insulation Board.]

#### [Polyisocyanurate thermal insulation boards must meet or exceed requirements of CAN/ULC S704-011, Thermal Insulation, Polyurethane and Polyisocyanurate, Boards Faced].

#### [Extruded polystyrene insulation boards must meet or exceed requirements of CAN/ULC-S701-11, Expanded Polystyrene Insulation Board and Pipe Covering.]

#### [Roofing system must meet or exceed requirements of CAN/ULC-S107-10, Methods of Fire Tests of Roof Coverings, Class [A] [B] [C].]

## COMPATIBILITY

#### All waterproofing materials will be provided by the same manufacturer.

## TECHNICAL DOCUMENTS

#### Submit two (2) copies of the most current technical data sheets. These documents must describe the physical properties of materials [and explanations about product installation, including restrictions, limitations and other manufacturer recommendations].

## QUALITY ASSURANCE AND ENVIRONMENTAL MANAGEMENT

NOTE TO THE SPECIFIER: Certificates of qualification may be part of the documents required for submission. Where applicable, these requirements shall be part of the call for tender(s).

#### The manufacturer of elastomeric bitumen products will provide proof of ISO 9001 and ISO 14001 Certifications.

## CONTRACTOR QUALIFICATIONS

#### Roofing contractors and sub-contractors must, when tendering and during works, possess a roofing contractor operating license.

#### [Roofing contractors and sub-contractors must also be registered with SOPREMA’s PAQ + S program, and provide the architect with a written certificate issued by SOPREMA to this effect before beginning any roofing work.]

## MATERIALS STORAGE AND DELIVERY

#### All materials will be delivered and stored in their original packaging, in conformance with the requirements described in the manufacturer’s technical documentation.

#### At all times, materials will be adequately protected and stored in a dry and properly ventilated area, away from any welding flame or spark, and sheltered from the elements and any harmful substances.

#### Store adhesives and solvent-based mastics at a minimum of 5 °C (41 °F).

#### Materials delivered in rolls will be carefully stored upright; flashings will be stored to avoid wrinkling, buckling, scratches or any other possible damage.

#### Avoid gathering construction materials on the roof, which may affect the structural integrity by imposing loads exceeding what is admissible.

## FIRE PROTECTION

#### Prior to the start of work, conduct a site inspection to ensure its safety in order to minimize fire risks and hazards.

#### Respect safety measures recommended by the related local authorities.

#### At the end of each workday, use a heat detector gun to spot any smouldering or concealed fire. Job planning must be organized to ensure workers are still on location at least […] hour[s] after welding works. An inspection must be performed by an employee of the roofing contractor who specializes in this kind of job at the end of works and, if necessary, with the help of a member of the fire protection service of the city.

#### Never apply the torch directly to flammable materials.

#### Throughout roofing installation, maintain a clean site and have a fire hose (when possible) and at least one ULC-approved Class A, B or C fire extinguisher, charged and in perfect operating condition, within 6 m (20 ft) of each torch. Respect all safety measures described in technical data sheets of sealants. Welding torches must never be placed near combustible or flammable products, nor be used where the flame is not visible or cannot be easily controlled.

## WARRANTIES

NOTE TO THE SPECIFIER: Please refer to the National Master Specifications (NMS) for federal government contracts. For other works, please refer to the following term(s). For more information on roofing membrane warranty, please consult SOPREMA's warranties (of which terms must in no way be modified).

NOTE TO THE SPECIFIER: Retain the following article when a material and workmanship warranty (SOPREMA PLATINUM WARRANTY) is requested (warranty of the membrane manufacturer).

#### The membrane manufacturer will issue a written document in the owner’s name, valid for a [   ]-year period, stating that it will repair any leaks in the roofing membrane to restore the roofing system to a dry and watertight condition, to the extent that manufacturing or installation defects caused such water infiltration. The warranty must cover the total cost of repair(s) during the entire warranty period. The warranty must be transferable, at no extra cost, to subsequent building owners. The warranty certificate must reflect these requirements.

NOTE TO THE SPECIFIER: Retain the following article when requesting a materials warranty (warranty from the membrane manufacturer).

#### The membrane manufacturer will issue a written and signed document in the owner's name, certifying that the roofing membranes are free of manufacturing defects for a period of ten (10) years, starting from the date of completion of membrane installation. This warranty will cover the removal and replacement of defective roof membrane products, including workmanship. The warranty must remain full and complete for the duration of the period specified. The warranty certificate must reflect these requirements.

NOTE TO THE SPECIFIER: Retain the following article when requesting a workmanship warranty (warranty from the roofing contractor).

#### The contractor will provide a written and signed document to the owner’s name certifying that the work executed will remain in place and free of waterproofing defect for a [   ]-year period from the date of acceptance.

NOTE TO THE SPECIFIER: Some local roofing associations issue waterproofing warranties complementary to those previously mentioned. Please consult these local associations for the terms and conditions of these warranties.

#### [The contractor will provide [local association] a certificate of warranty for this project, valid for a [   ]-year period.]

# Products

## VAPOUR BARRIER SUPPORT PANELS

NOTE TO THE SPECIFIER: When specifying XPRESS VAP’R BOARD as “Vapour Barrier Support Panel”, use the “Vapour Barrier” Section of the specification.

### Lightweight Concrete Panel

#### Description : Non combustible lightweight concrete panel in in conformance with CAN/ULC-S114-05 « Standard Method of Test for Determination of Non-Combustibility in Building Materials ».

#### Specified product: Perma Base Dek by Unifix

### Gypsum-Fibre Roof Board

#### Description: glass fibre-covered roof board [ [ ]-mm-thick].

#### In conformance with: ASTM E84 and ASTM C1177

#### Specified product:

## VAPOUR BARRIER

NOTE TO THE SPECIFIER: Choose the vapour barrier best suited to roof substrate, and that meets possible ULC and/or FM requirements, if needed. Take into consideration humidity conditions of adjacent premises as well as general installation conditions.

### Thermal Barrier and Vapour Barrier Board

#### Description: Board of a minimum thickness of 15.8 mm (5/8 in) composed of SBS modified bitumen membrane with a polyester reinforcement, factory-laminated on a mineral wool board. The membrane measures 1 m by 4.91 m (3.28 ft x 16.10 ft). The top face is sanded. The membrane side lap is part self-adhesive and part thermofusible.

#### Specified product: XPRESS VAP’R BOARD by SOPREMA.

NOTE TO THE SPECIFIER: The vapour-barrier membrane below is self-adhesive and does not require torching or hot bitumen. However, it cannot be used under insulation board adhered with hot asphalt. Also consider application temperature limitations.

### Self-Adhesive Vapour Barrier

#### Description: Self-adhesive membrane composed of SBS modified bitumen, with a surface screen made of high-density polyethylene laminated between two layers of polyethylene films. The width of the membrane is 1.14 m (45 in) to allow the membrane to fit on the top of most structural steel deck profiles. The self-adhesive underface is protected with a silicone plastic release film.

#### Specified product: SOPRAVAP’R by SOPREMA.

### Modified Bitumen Vapour Barrier

#### Description: Roofing membrane composed of SBS modified bitumen and a [composite] [non-woven polyester] [glass mat] reinforcement. Both surfaces are sanded.

#### In conformance with: CAN/CGSB 37.56-M (9th Draft).

#### Specified product(s): [COLPLY BASE 410] [SOPRALENE 180 SANDED] [ELASTOPHENE SANDED] by SOPREMA.

NOTE TO THE SPECIFIER: A glass mat with oxidized bitumen can be set on hot asphalt and used as a vapour barrier, as specified below. This more economical type of vapour barrier contains no organic matter that could deteriorate with exposure to possible water infiltrations in the roof.

### Oxidized Bitumen Vapour Barrier

#### Description: [Oxidized bitumen and glass mat-reinforced membrane. Nominal thickness of [1.2 mm (0.04 in)] [1.5 mm (0.06 in)]. Both surfaces are sanded.]

#### Specified product: SOPRAGLASS [40] [100] by SOPREMA.

NOTE TO THE SPECIFIER: The vapour barrier below can be specified for buildings with low humidity levels; this type of vapour barrier can also be used with assemblies conforming to ULC and FM standards where no fire separations are required (gypsum board or other) and where certain insulations are installed directly onto steel deck. These assemblies are more economical overall.

### Kraft Paper Vapour Barrier

#### Description: [Vapour barrier composed of two layers of high moisture resistance Kraft paper bonded together with asphalt.]

#### In conformance with: ASTM E96.

#### Specified product: SOPRASTOP by SOPREMA.

NOTE TO THE SPECIFIER: Install a self-adhesive membrane strip beneath parapets and at wall junctions to ensure vapour barrier continuity, as specified below. For on-site co-ordination, this membrane must be provided by the roofer and installed by a carpenter. Specify the installation of this strip in the Carpentry Section.

### Vapour Barrier Continuity Strip

#### Description: Waterproofing membrane with composite reinforcement and SBS modified bitumen. The surface is sanded and the underface is self-adhesive and covered with a silicon release film.

#### Specified product: SOPRALENE STICK ADHESIVE by SOPREMA.

## INSULATION

### Mineral Wool Roof Insulation Board with Weldable Surface

#### Description: Mineral wool roof insulation board with a rigid surface made from basalt rock and steel slag. The surface is impregnated with a bitumen layer which is compatible with membranes applied with a torch, hot bitumen or adhesive.

#### Specified product: SOPRAROCK DD PLUS by SOPREMA

### Mineral Wool Roof Insulation Board

#### Description: Mineral wool roof insulation board with a rigid surface made from basalt and steel slag.

#### Specified product: SOPRAROCK DD by SOPREMA

### Mineral Wool Roof Insulation

#### Description: Mineral wool-based roof support panel with a homogeneous density made from basalt and steel slag.

#### Specified product: SOPRAROCK MD by SOPREMA

### Polyisocyanurate Insulation

#### Description: Closed-cell polyisocyanurate foam insulation board laminated on both sides with a fiberglass yarn-reinforced organic paper.

#### Specified product: SOPRA-ISO by SOPREMA

### Tapered Insulation Board

#### Description : Tapered insulation panel made of [mineral wool] [polyisocyanurate] designed to create a [   ] percent (%) slope to the roof system.

#### Specified product : [             ]

### Sump Insulation Board for Drain Location

#### Description: Sump insulation panel made of [mineral wool] [polyisocyanurate] designed to facilitate proper drainage around drain.

#### Product specified : [             ]

## INSULATION SUBSTRATE OVERLAY

NOTE TO THE SPECIFIER: The board described below can be used in roof repair as a base membrane over the existing waterproofing membranes. It is suitable as a support for thermofusible and self-adhesive membranes or those installed with cold adhesive or hot bitumen.

### Bituminous Board

#### Description: Semi-rigid roofing support panel composed of a mineral-reinforced asphaltic core between two asphalt-saturated fibreglass liners. Length of 1.2 m (3.93 ft), width of [1.5 m (4.92 ft)] [2.43 m (7.97 ft)] and thickness of [3.2 mm (0.12 in)] [4.8 mm (0.18 in)] [6.4 (0.25 in)].

#### Specified product: SOPRABOARD by SOPREMA.

### Mineral Board with Weldable Surface

#### Description: Rigid mineral wool fibre board, manufactured from basalt and steel slag with a surface saturated with bitumen which is compatible with membranes applied with a torch, hot bitumen or adhesive.

#### Specified product: SOPRAROCK MD PLUS by SOPREMA.

### Wood Fibre Board [impregnated with fire retardant]

#### Description: Wood fibre board, [   ] x [   ] x [   ] in thickness.

#### In conformance with: [CAN/ULC S706-09] [CAN/CSA A247-M86] standard.

#### Specified product: [       ].

### Expanded Perlite Board

#### Description: Expanded perlite board, [   ] x [   ] x [   ] in thickness.

#### In conformance with: ASTM C728-11 standard.

#### Specified product: [       ].

## MEMBRANES

### Base Sheet Membrane for Field Surface

#### Description: Roofing membrane composed of SBS modified bitumen and a composite reinforcement. Both sides are sanded. The surface must be marked with three (3) chalk lines to ensure proper roll alignment.

#### In conformance with: CGSB 37.56-M (9th Draft).

#### Properties: 							MD 		XD

###### Strain energy (kN/m)		7.8	7.2

###### Breaking strength (kN/m)	15 	13.5

###### Ultimate elongation (%)		60 	65

###### Tear resistance (N)		125

###### Static puncture resistance (N)	560

###### Dimensional stability (%)	0.2	0

###### Plastic flow (°C)		≥ 110

###### Cold bending at -30 °C		No cracking

###### Lap joint strength (kN/m) 	Pass > 4 kN/m

#### Specified product: COLPLY BASE 410  by SOPREMA

### Base Sheet Membrane for Flashings and Parapets

#### Description: Membrane composed of SBS modified bitumen and [composite] [glass mat] reinforcement. [Both sides are] [The surface is] sanded and the underface is [covered with a release protection film] [sanded]. The surface shall be marked with three (3) chalk lines to ensure proper roll alignment.

#### In conformance with: CGSB 37.56-M (9th Draft).

#### Properties: 							MD 		XD

###### Strain energy (kN/m)		[  ]	[  ]

###### Breaking strength (kN/m)	[  ] 	[  ]

###### Ultimate elongation (%)		[  ] 	[  ]

###### Tear resistance (N)		[  ]

###### Static puncture resistance (N)	[  ]

###### Dimensional stability (%)	[  ] 	[  ]

###### Plastic flow (°C)		≥ [    ]

###### Cold bending at -30 °C		No cracking

###### Lap joint strength (kN/m)	[  ]

#### Specified product: [SOPRAFLASH STICK] [COLPLY BASE 410] [SOPRALENE STICK ADHESIVE] by SOPREMA

### Roofing Cap Sheet Membrane for Field Surfaces

#### Description: Roofing membrane composed of SBS modified bitumen and a composite reinforcement. Both sides are sanded. The surface must be marked with three (3) chalk lines to ensure proper roll alignment.

#### In conformance with: CGSB 37.56-M (9th Draft).

#### Properties: 							MD 		XD

###### Strain energy (kN/m)		7.8	7.2

###### Breaking strength (kN/m)	15 	13.5

###### Ultimate elongation (%)		60 	65

###### Tear resistance (N)		125

###### Static puncture resistance (N)	560

###### Dimensional stability (%)	0.2	0

###### Plastic flow (°C)		≥ 110

###### Cold bending at -30 °C		No cracking

###### Lap joint strength (kN/m) 	Pass > 4 kN/m

#### Specified product: COLPLY BASE 410  by SOPREMA

### Roofing Cap Sheet Membrane for Flashings and Parapets

#### Description: Roofing membrane composed of SBS modified bitumen and a composite reinforcement. The surface is protected by coloured granules. The underface  is sanded.

#### In conformance with: CGSB 37.56-M (9th Draft).

#### Properties: 							MD 		XD

###### Strain energy (kN/m)		7.8	7.2

###### Breaking strength (kN/m)	15 	13.5

###### Ultimate elongation (%)		60 	65

###### Tear resistance (N)		125

###### Static puncture resistance (N)	560

###### Dimensional stability (%)	0.2	0

###### Plastic flow (°C)		≥ 110

###### Cold bending at -30 °C		No cracking

###### Lap joint strength (kN/m) 	Pass > 4 kN/m

#### Specified Product: COLPLY TRAFFIC CAP 460 by SOPREMA

## ACCESSORY MEMBRANES

## PRIMER

### Primer for Thermofusible Membranes

#### Description: Primer made of bitumen, volatile solvents and adhesive resins. Used as primer to improve the adhesion of thermofusible waterproofing membranes.

#### Specified product: ELASTOCOL 500 by SOPREMA.

### Primer for Self-Adhesive Membranes

#### [Description: Primer composed of SBS synthetic rubber, adhesive resins and volatile solvents. Used as primer to improve the adhesion of self-adhesive membranes.]

#### Specified product: ELASTOCOL STICK by SOPREMA.

#### [Description: Primer composed of SBS synthetic rubber, adhesive resins and VOC-free solvents. Used as primer to improve the adhesion of self-adhesive membranes.

#### Specified product: ELASTOCOL STICK ZERO by SOPREMA

#### [Description: Polymeric emulsion composed of SBS synthetic rubber and adhesive resins. Used as primer to improve the adhesion of self-adhesive membranes.]

#### Specified product: ELASTOCOL STICK H20 by SOPREMA

## [BITUMEN] [ASPHALT]

NOTE TO THE SPECIFIER: Use oxidized asphalt or SEBS bitumen to adhere insulation and membrane supports. Use only SEBS bitumen to adhere a cap sheet to a modified bitumen base sheet. Use Type 2 oxidized asphalt for slopes ( 2% and Type 3 oxidized asphalt for slopes between 2% and 25%.

### Oxidized Asphalt

#### Description: Bitumen used for waterproofing of multilayer coatings for Type [2] [3] roofing systems.

#### In conformance with: CAN/CSA-A123.4-F04 (C2008)

#### Specified product: [         ]

NOTE TO THE SPECIFIER: Specify SEBS bitumen for membranes and slopes of up to 25%. This type of bitumen has superior flexibility and greater durability than Type 2 or 3 asphalt.

### SEBS Bitumen

#### Description: SEBS modified bitumen used as roofing cement.

#### Specified product: SOPRASPHALTE M by SOPREMA

## ADHESIVES

NOTE TO THE SPECIFIER: COLTACK is intended for use as a cold adhesive for polyisocyanurate insulation. It is not recommended for polystyrene insulation. It is also suitable to fix these boards on wood, concrete or the sanded surface of elastomeric bitumen membranes. Minimum application temperature: 5 °C (41 °F).

### Insulation Adhesive

#### Description: Cold-applied, solvent-based polyurethane resin bituminous adhesive.

#### Specified product: COLTACK by SOPREMA.

NOTE TO THE SPECIFIER: DUOTACK is intended for use as a cold adhesive to fix polyisocyanurate and polystyrene (expended and extruded) insulations. It is also suitable to fix these boards on wood, concrete or sanded surfaces of elastomeric bitumen membranes. DUOTACK can be applied at any temperature.

### Insulation Adhesive

#### Description: Two-component, quick-setting, low-expansion foam urethane adhesive that can be applied at any temperature.

#### Specified product: DUOTACK by SOPREMA

## FASTENERS

### Insulation Fasteners

#### Description: [              ]

#### Specified products: [              ]

## COMPLEMENTARY WATERPROOFING PRODUCTS

NOTE TO THE SPECIFIER: Use the product described below for all sealing products in contact with the waterproofing membrane. It is recommended to cover SOPRAMASTIC with granules when it is left exposed. Aluminum pigments are added to SOPRAMASTIC ALU to provide roofing elements a greater resistance; it can be left exposed.

### Waterproofing Mastic

#### Description: Multi-purpose mastic composed of SBS modified bitumen, fibres, [aluminium pigments,] mineral fillers and solvents.

#### Specified product: SOPRAMASTIC [ALU] by SOPREMA

### Pitch Pocket Filler

#### Description: Polyester-made precast blocks of various sizes a single-component, polyether-based mastic and a single-component, polyether based sealant and adhesive.

#### Specified product: SOPRAMASTIC BLOCK SYSTEM by SOPREMA

### Sealing Product

#### Description: Bitumen/polyurethane waterproofing mono-component resin and polyester reinforcement.

#### Specified products: ALSAN FLASHING and ALSAN REINFORCEMENT by SOPREMA

## BALLAST

### Gravel (Crushed Stone)

#### Description: Hard aggregates; washed, clean, non-porous and free of overlong fragments, dust, humidity, ice, snow and any foreign object. They shall come from a recognized quarry and be intended for making concrete. Grain size shall be as specified below (any variance must be previously approved by the [owner] [architect]).

#### Grain size: [              ]

# Execution of Work

## SURFACE EXAMINATION AND PREPARATION

#### Surface examination and preparation must be completed in conformance with instructions in the membrane manufacturer’s technical documentation.

#### Before roofing work begins, the owner's representative and roofing foreman will inspect and approve deck conditions (including slopes and wood grounds) as well as flashings at parapets, roof drains, plumbing vents, ventilation outlets and other construction joints. If necessary, a non-conformity notice will be issued to the contractor so that required corrections can be carried out. The start of roofing work will be considered as acceptance of conditions for work completion.

#### Do not begin any portion of work before surfaces are clean, smooth, dry, and free of ice and debris. Use of calcium or salt is forbidden for ice or snow removal.

#### Be sure plumbing, carpentry and all other works have been duly completed.

#### No materials will be installed during rain or snowfall.

## METHOD OF EXECUTION

NOTE TO THE SPECIFIER: When demolition work is required, or when work is needed on existing materials, be sure to respect the requirements of the Workplace Hazardous Materials Information System (WHMIS). Refer to Section 01545: Safety Measures in the NMS.

NOTE TO THE SPECIFIER: Refer to membrane manufacturer for pertinent specifications (according to site conditions) when base sheet membranes remain exposed without cap sheet for more than three (3) months.

#### Roofing work must be completed in a continuous fashion as surfaces are readied and as weather conditions allows it.

#### It’s preferable to seal all joints that are not covered by a cap sheet membrane the same day. A second cap sheet cannot be installed if any moisture is present in joints.

NOTE TO THE SPECIFIER: Please retain the following clause in case of re-roofing where underlying structures must be protected.

#### Ensure waterproofing of roofs at all times, including protection during installation work by other trades and protection as work is completed (e.g. vents, drains, etc.).

## SITE PROTECTION

#### Protect the exposed surfaces of finished work to avoid damage during roof installation and material transportation. [Install walkways made of rigid boards over installed roofing materials to enable passage of people and transport of products.] Assume full responsibility for any damage.

## PREPARATION WORK – METAL DECK

#### [Install acoustic insulation in deck flutes.]

## PREPARATION WORK – CONCRETE DECK

#### Prepare surfaces according to [manufacturer’s] [local authorities’] recommendations. Surfaces to be waterproofed with elastomeric bitumen membrane must have a Concrete Surface Profile (CSP) of 3 to 6 (CSP as per the International Concrete Repair Institute).

## INSTALLATION OF VAPOUR BARRIER SUPPORT PANELS ON STEEL DECK

#### Adhere support panel using specified adhesive applied in continuous strips spaced [    ] on the field surface, [    ] on the perimeter, and [    ] on corners.

#### These boards must be screwed onto the steel deck's upper rib surfaces [at a rate of [    ] mechanical fasteners per board] [, in conformance with Factory Mutual requirements, including the PLPDS 1-29, for fastening boards at roof corners and perimeters].

#### Cut boards so edges rest on centre of upper ribs. Cut straight lines with adequate tools.

#### Where slopes change, boards will be cleanly cut (avoid breaking boards) to acquire deck shape. Place boards perpendicular to deck ribs for continuous support at extremities.

#### Board joints will be staggered, at half-length, and perfectly butted. [Joints will be sealed with heat-resistant tape in both directions to prevent any asphalt leakage in finished areas.]

## APPLICATION OF PRIMER

NOTE TO THE SPECIFIER: Please refer to Technical Data Sheets for application rate of specified products.

#### Wooden, metallic, concrete, and masonry surfaces or gypsum insulation substrate will receive a coat of primer at a rate of [    to    ] L/m2 (no primer is required for factory-painted metals). All surfaces to be primed must be free of rust, dust or any residue that may hinder adherence. Primed surfaces must be covered with the roofing membrane as soon as possible (on the same day for self-adhesive membranes).

NOTE TO THE SPECIFIER: Use the following article when a self-adhesive vapour barrier is specified. Make sure that the substrate is approved for this type of installation.

## Installation of Self-Adhesive Vapour Barrier

#### Primer must be dry prior to the installation of the vapour barrier membrane.

#### Starting at the bottom of the slope, without adhering the membrane, unroll it onto the substrate for alignment. Do not immediately remove the silicone release film.

#### Align the roll parallel to the ribs of the steel deck. Make sure membrane overlaps are supported along their entire length.

#### Remove one end of the silicone release film and adhere this part of the membrane to the substrate. Remove the remaining release film at a 45º angle to avoid wrinkles in the membrane.

#### Overlap adjacent rolls of 75 mm (3 in) and 100 mm (4 in). End laps must be 150 mm (6 in). Space end laps by at least 300 mm (12 in).

#### When the vapour barrier is installed directly on a steel deck, place a thin sheet of metal under the end laps of the vapour barrier.

## Installation of Hot-Bitumen Vapour Barrier

#### Primer must be dry prior to the installation of the vapour barrier membrane.

#### Starting at the lowest point of the roof, unroll vapour barrier onto hot asphalt layer spread at rate of 1 kg/m2 (2.20 lb/ft2) to 1.5 kg/m2 (3.30 lb/ft2).

#### Apply asphalt on the roof at a temperature of about 230 °C (446 °F) heated in a boiler at about 250 °C (482 °F) (never exceed asphalt’s flash point temperature). Follow supplier's recommendations. In cold weather (below 10 °C [50 °F]), warm membrane's underface by sweeping the flame of a torch over the entire width of a roll.

#### Overlap adjacent rolls by 75 mm (3 in). End laps must be 150 mm (6 in). Space end laps by at least 300 mm (12 in).

#### The roof vapour barrier must meet and overlap the air/vapour barrier on adjoining walls to ensure total continuity. Roofing cement and membrane must not exceed field surface base sheet by more than 25 mm (1 in).

#### Install vapour barrier at insulation perimeters and around each element penetrating the insulation to ensure sealed connections with flashing base sheet.

#### Roofing cement and membrane must not exceed flashing base sheet by more than 25 mm (1 in).

## Installation of Asphalted Kraft Vapour Barrier

NOTE TO THE SPECIFIER: Consult the manufacturer as needed for required instructions related to specified vapour barrier.

#### [Adhere vapour barrier to substrate with specified adhesive in conformance with manufacturer's recommendations.] [Adhere the vapour barrier to substrate and seal joints with recommended adhesive in conformance with manufacturer's recommendations.]

## Installation of Support Panel and Vapour Barrier

NOTE TO THE SPECIFIER: Use the following clause when boards are mechanically fastened to wooden or steel substrates.

#### Mechanically fasten boards with screws and plates for membranes. [Mechanical fasteners must be installed in the centre of the membrane side selvedge [and on board surface] at a rate of [    ] on the field surface, [    ] on the roof perimeter, and [    ] on corners.] [Follow instructions of approval reports for location of fasteners.]

NOTE TO THE SPECIFIER: Use the following clause when boards are installed on substrate using adhesive

#### Adhere boards by using specified adhesive in continuous strips spaced [    ] on the field surface, [    ] on the perimeter, and [    ] on corners. [Corners and perimeters must be installed as per FM requirements listed in the PLPDS 1-29].

#### Because of the nature of this system, for this type of vapour barrier, joints can be aligned (no offset) to facilitate the installation of the reinforcing strip.

#### Adhere the first part of the self-adhesive side laps using a membrane roller, then heat-weld the last part (self-adhesive, heat-welded side laps).

#### Seal the end laps by welding a 330-mm (13-in) wide protection strip centered on the joint.

## INSTALLATION OF INSULATION

NOTE TO THE SPECIFIER: Use the following clause when insulation is installed on substrate using adhesive. Check if this type of adhesive is appropriate for that type of application.

#### [Adhere insulation by using specified adhesive in continuous strips spaced [    ] on the field surface, [    ] on the perimeter, and [    ] on corners. [Corners and perimeters must be installed as per FM requirements listed in the PLPDS 1-29].

NOTE TO THE SPECIFIER: Use the following clause when boards are mechanically fastened to the substrates.

#### [Mechanically fasten boards with screws and plates for membranes, at a rate of [    ] on the field surface [, [    ] on the perimeter, and [    ] on corners]. [Corners and perimeters must be installed as per FM requirements listed in the PLPDS 1-29.] [Screws must be driven in deck's upper flutes.]]

NOTE TO THE SPECIFIER: Use the following clause when insulation boards and panels with factory-laminated membrane are mechanically fastened to the substrate.

#### [It is not required to fasten insulation boards to achieve wind uplift resistance when base sheet membranes are mechanically fastened. However, in order to prevent any insulation board movement, they can be fastened at a rate of one fastener per 4 ft2.]

NOTE TO THE SPECIFIER: Use the following clause when boards are adhered to substrate with hot asphalt.

#### [On the whole surface of the vapour barrier corresponding to the surface of the insulation block to be applied, apply a coat of hot asphalt at a rate of 1 kg/m2 (2.20 lb/ft2), according to methods and temperatures recommended by the manufacturer.]

#### All boards must be in perfect connection, without any significant variances in level, and must be completely adhered to the surface.

#### [All vertical joints between [flat boards and sloped modules] [the two rows of insulation boards] will be staggered.]

#### [Around the drain, execute a slight slope of 0 to 10 mm (0 to 0.4 in) in a 600-mm (24-in) radius.]

#### Install only as much insulation as can be covered in the same day.

## SUMP INSULATION PANEL INSTALLATION

#### Install sump insulation panel in conformance with manufacturer’s instructions and recommendations

## INSTALLATION OF SUPPORT PANELS

NOTE TO THE SPECIFIER: Use the following clause when insulation is installed on substrate using adhesive. Check if this type of adhesive is appropriate for that type of application.

#### Adhere support panel using specified adhesive applied in continuous strips spaced [    ] on the field surface [    ] on the perimeter, and [    ] on corners]. [Corners and perimeters must be installed as per FM requirements listed in the PLPDS 1-29.]

NOTE TO THE SPECIFIER: Use the following clause when boards are mechanically fastened to the substrate.

#### [Mechanically fasten support panels at a rate of [    ] fasteners per board on the field surface] [, [    ] on the perimeter, and [    ] on corners]. Corners and perimeters must be installed as per FM requirements listed in the PLPDS 1-29.] [Screws must be driven into deck's upper flutes.]

NOTE TO THE SPECIFIER: Use the following clause when boards are adhered to substrate with hot asphalt.

#### [On the whole surface of the insulation corresponding to the support panel surface to be installed, apply a coat of hot asphalt at a rate of 1 kg/m2 (2.20 lb/ft2), following methods and temperatures recommended by the manufacturer.]

#### All boards must be in perfect connection, without any significant variances in level, and must be completely adhered to the surface.

#### [All vertical joints between [flat boards and sloped modules] [the two rows of insulation boards] will be staggered.

#### Install only as much insulation as can be covered in the same day.

## INSTALLATION OF [SEBS BITUMEN] [HOT ASPHALT] BASE SHEET ON FIELD SURFACE

#### Unroll base sheet onto substrate, taking care to align the edge of the first selvedge with drain centre (parallel to roof edge).

#### Cut off corners at end laps to be covered by the next roll.

#### Re-roll base sheet and unroll again onto a layer of [hot asphalt] [SEBS bitumen] applied before unrolling. Minimum temperature of [hot asphalt] [SEBS bitumen] at point of contact should be 220-230°C (428-446 °F).

#### Do not spread more than 3 m (10 ft) of [hot asphalt] [bitumen] in front of each roll. For temperatures below 10 °C (50 °F), do not spread more than 1 m (3.3 ft) of [hot asphalt] [bitumen] in front of each roll.

#### [Hot asphalt] [Bitumen] must never be applied on thermofusible film or exceed by 25 mm (1 in) from vertical parts of the base-sheet membrane of field surfaces.

#### Each selvedge will overlap the previous one along lines provided for this purpose, and will overlap by 150 mm (6 in) at the ends. Space end laps by a minimum of 300 mm (12 in).

#### Avoid the formation of wrinkles, swellings or fishmouths.

## INSTALLATION OF SELF-ADHESIVE BASE SHEET ON FLASHINGS AND PARAPETS

#### Apply base sheet flashing only after primer coat is dry.

#### Before applying membranes, always burn the plastic film from the section to be covered if there is an overlap (inside and outside corners and field surface). For sanded base sheet membranes, apply primer for self-adhesive membrane on the area to be covered at the foot of the parapets.

#### Cut off corners at end laps of areas to be covered by the next roll.

#### Each selvedge will overlap the previous one along lines provided for this purpose, and by 150 mm (6 in) at the ends.

#### Position the pre-cut membrane. Remove 150 mm (6 in) of the silicone release film to hold the membrane in place at the top of the parapet.

#### Then, gradually peel off the remaining silicone release film, pressing down on the membrane with an aluminum applicator to ensure good adhesion. Use the aluminum applicator to ensure a perfect transition between the flashing and the field surface. Smooth the entire membrane surface with a membrane roller for full adhesion.

#### Install a reinforcing gusset at all inside and outside corners.

#### Always seal overlaps at the end of the workday.

#### Avoid the formation of wrinkles, swellings or fishmouths.

## INSTALLATION OF SEBS BITUMEN BASE SHEET ON FLASHINGS AND PARAPETS

#### Cut off corners at end laps of areas to be covered by the next roll.

#### Each selvedge will overlap the previous one along lines provided for this purpose, and by 150 mm (6 in) at the ends.

#### Use a TARZAN roller to spread SEBS bitumen on the surfaces of the parapets and other flashings. For inside and outside corners, use a stiff-bristled brush to spread the bitumen over the overlap joints. Do not spread more than 1 m (3.3 ft) at a time. Immediately proceed with the subsequent application steps before the bitumen cools down.

#### Position the pre-cut membrane at the top of the parapet. Progressively press down on the membrane from top to bottom using an aluminum applicator to ensure good adhesion. Use the aluminum applicator to ensure a perfect transition between the flashing and the field surface.

#### Install a reinforcing gusset at all inside and outside corners.

#### Avoid the formation of wrinkles, swellings or fishmouths.

## INSTALLATION OF REINFORCED GUSSETS

#### Install reinforcing gussets at all inside and outside corners.

## INSTALLATION OF SEBS BITUMEN CAP SHEET ON FIELD SURFACE

#### Unroll base sheet onto substrate, taking care to align the edge of the first selvedge with drain centre (parallel to roof edge).

#### Cut off corners at end laps to be covered by the next roll.

#### Re-roll base sheet and unroll again onto a layer of [hot asphalt] [SEBS bitumen] applied before unrolling. Minimum temperature of [hot asphalt] [SEBS bitumen] at point of contact should be 220-230°C (428-446 °F).

#### Do not spread more than 3 m (10 ft) of [hot asphalt] [bitumen] in front of each roll. For temperatures below 10 °C (50 °F), do not spread more than 1 m (3.3 ft) of [hot asphalt] [bitumen] in front of each roll.

#### [Hot asphalt] [Bitumen] must never be applied on thermofusible film or exceed by 25 mm (1 in) from vertical parts of the base-sheet membrane of field surfaces.

#### Each selvedge will overlap the previous one along lines provided for this purpose, and will overlap by 150 mm (6 in) at the ends. Space end laps by a minimum of 300 mm (12 in).

#### Avoid the formation of wrinkles, swellings or fishmouths.

## INSTALLATION OF SEBS BITUMEN CAP SHEET ON FLASHINGS AND PARAPETS

#### This cap sheet must be installed in one-metre-wide strips (3.25 ft).

#### Each selvedge will overlap the previous one laterally along lines provided for this purpose, and will overlap by 150 mm (6 in) the field surface. Cap sheet membranes for flashings must be spaced by at least 100 mm (4 in) with respect to the cap sheet membranes on the field surface, to avoid areas of excessive membrane thickness.

#### Cut off corners at end laps of areas to be covered by the next roll.

#### Use a chalk line to draw a straight line on the field surface 150 mm (6 in) from the flashings and parapets.

#### Use a TARZAN roller to spread SEBS bitumen on the surfaces of the flashing. For inside and outside corners, use a stiff-bristled brush to spread the bitumen over the overlap joints. Do not spread more than one metre (3.28 ft) at a time. Immediately proceed with the subsequent application steps before the bitumen cools down.

#### Position the pre-cut membrane at the top of the parapet. Progressively press down on the membrane from top to bottom using an aluminium applicator to ensure good adhesion. Use the aluminium applicator to ensure a perfect transition between the flashing and the field surface.

#### During installation, take care to avoid excessive bitumen dripping at joints.

## INSTALLATION OF BITUMEN AND GRAVEL (CRUSHED STONES)

#### Spread bitumen in a uniform fashion at a rate of 3 kg/m2 (60 lb/100 ft2). Spread gravel in a uniform fashion at a rate of 27 kg/m2 (500 lb/100 ft2) directly onto hot bitumen.

## WATERPROOFING FOR VARIOUS DETAILS

#### Install waterproofing membranes at various roofing details in conformance with typical details indicated in technical documentation of the manufacturer.

Note: Based on the evolution of knowledge and techniques, SOPREMA INC. may modify the composition and/or conditions of use of its products without prior notice. Consequently orders will be filled according to the latest specifications.

- END OF SECTION -