XPRESS BOARD HD

SOPRAPLY TRAFFIC CAP 560

SPECIFICATIONS

THESE MASTER SPECIFICATIONS CONTAIN ALL SPECIFICATIONS FOR EACH SPECIFIC SOPREMA ROOFING MEMBRANE SYSTEM.

THE EDITOR SHOULD CONTACT A SOPREMA REPRESENTATIVE TO GET ASSISTANCE FOR THE ADAPTATION OR COMPLETION OF SPECIFICATIONS ACCORDING TO THE PARTICULAR CONDITIONS RELATED TO EACH PROJECT.

IMPORTANT: PLEASE BE SURE TO READ THE POLICY STATEMENT IN THE IMPORTANT NOTICES SECTION IN THE FIRST PAGES OF THE SOPREMA RING BINDER.

FOR A COMPLETE DESCRIPTION OF PRODUCTS AND APPLICABLE STANDARDS, PLEASE REFER TO THE TECHNICAL DATA SHEETS ON OUR WEBSITE AT WWW.SOPREMA.CA.

THE ELECTRONIC VERSION OF OUR SPECIFICATIONS IS ALSO AVAILABLE ON SOPREMA’S WEBSITE.

# General

## REFERENCE STANDARD[S]

NOTE TO THE SPECIFIER: The designer of the waterproofing system should investigate with the client which requirements apply to a particular project. Applicable building regulations must be followed. Consult provincial roofing associations, since they could have special requirements, particularly if they offer warranties.

NOTE TO THE SPECIFIER: The National Building Code requires that all roofs, except when permitted (tents, inflatable structures, certain small “assembly occupancy” buildings), must be either Class A, B, or C, as determined in accordance with CAN/ULC-S107-03 “Standard Methods of Fire Tests of Roof Coverings.”

#### [Submit a report, issued by a certified materials testing laboratory, attesting that the specified roofing system was tested in accordance with CSA A123.21-10, Standard test method for the dynamic wind uplift resistance of membrane-roofing systems. Test results shall demonstrate that the roofing system provides a Dynamic Uplift Resistance (DUR) of [   ] kPa for the field surface of the roof, [   ] kPa for the edges of the roof, and [   ] kPa for the corners of the roof.]

#### [Submit a report showing that the specified roofing system has been tested for Wind Uplift Resistance in accordance with FM 4470 Standard. The test results shall demonstrate that the roofing system provides a resistance of [   ] psf for the field surface of the roof. Edges and corners must be installed according to the requirements listed in FM PLPDS 1-29.]

#### [Membranes must meet or exceed requirements of CGSB 37.56–M (9th Draft), Membrane, Modified, Bituminous, Prefabricated, and Reinforced for Roofing.]

#### [Membranes must meet or exceed requirements of ASTM D 6162, Standard Specification for Styrene Butadiene Styrene (SBS) Modified Bituminous Sheet Materials Using a Combination of Polyester and Glass Fibre Reinforcements.]

#### [Membranes must meet or exceed requirements of ASTM D 6163, Standard Specification for Styrene Butadiene Styrene (SBS) Modified Bituminous Sheet Materials Using Glass Fibre Reinforcements.]

#### [Membranes must meet or exceed requirements of ASTM D 6164, Standard Specification for Styrene Butadiene Styrene (SBS) Modified Bituminous Sheet Materials Using Polyester Reinforcements.]

#### [Mineral wool roof insulation boards must meet or exceed requirements of ASTM C726, Standard Specification for Mineral Wool Roof Insulation Board.]

#### [Polyisocyanurate thermal insulation boards must meet or exceed requirements of CAN/ULC S704-011, Thermal Insulation, Polyurethane and Polyisocyanurate, Boards Faced].

#### [Extruded polystyrene insulation boards must meet or exceed requirements of CAN/ULC-S701-11, Expanded Polystyrene Insulation Board and Pipe Covering.]

#### [Roofing system must meet or exceed requirements of CAN/ULC-S107-10, Methods of Fire Tests of Roof Coverings, Class [A] [B] [C].]

## COMPATIBILITY

#### All waterproofing materials will be provided by the same manufacturer.

## TECHNICAL DOCUMENTS

#### Submit two (2) copies of the most current technical data sheets. These documents must describe the physical properties of materials [and explanations about product installation, including restrictions, limitations and other manufacturer recommendations].

## QUALITY ASSURANCE AND ENVIRONMENTAL MANAGEMENT

NOTE TO THE SPECIFIER: Certificates of qualification may be part of the documents required for submission. Where applicable, these requirements shall be part of the call for tender(s).

#### The manufacturer of elastomeric bitumen products will provide proof of ISO 9001 and ISO 14001 Certifications.

## CONTRACTOR QUALIFICATIONS

#### Roofing contractors and sub-contractors must, when tendering and during works, possess a roofing contractor operating license.

#### [Roofing contractors and sub-contractors must also be registered with SOPREMA’s PAQ + S program, and provide the architect with a written certificate issued by SOPREMA to this effect before beginning any roofing work.]

## MATERIALS STORAGE AND DELIVERY

#### All materials will be delivered and stored in their original packaging, in conformance with the requirements described in the manufacturer’s technical documentation.

#### At all times, materials will be adequately protected and stored in a dry and properly ventilated area, away from any welding flame or spark, and sheltered from the elements and any harmful substances.

#### Store adhesives and solvent-based mastics at a minimum of 5 °C (41 °F).

#### Materials delivered in rolls will be carefully stored upright; flashings will be stored to avoid wrinkling, buckling, scratches or any other possible damage.

#### Avoid gathering construction materials on the roof, which may affect the structural integrity by imposing loads exceeding what is admissible.

## FIRE PROTECTION

#### Prior to the start of work, conduct a site inspection to ensure its safety in order to minimize fire risks and hazards.

#### Respect safety measures recommended by the related local authorities.

#### At the end of each workday, use a heat detector gun to spot any smouldering or concealed fire. Job planning must be organized to ensure workers are still on location at least […] hour[s] after welding works. An inspection must be performed by an employee of the roofing contractor who specializes in this kind of job at the end of works and, if necessary, with the help of a member of the fire protection service of the city.

#### Never apply the torch directly to flammable materials.

#### Throughout roofing installation, maintain a clean site and have a fire hose (when possible) and at least one ULC-approved Class A, B or C fire extinguisher, charged and in perfect operating condition, within 6 m (20 ft) of each torch. Respect all safety measures described in technical data sheets of sealants. Welding torches must never be placed near combustible or flammable products, nor be used where the flame is not visible or cannot be easily controlled.

## WARRANTIES

NOTE TO THE SPECIFIER: Please refer to the National Master Specifications (NMS) for federal government contracts. For other works, please refer to the following term(s). For more information on roofing membrane warranty, please consult SOPREMA's warranties (of which terms must in no way be modified).

NOTE TO THE SPECIFIER: Retain the following article when a material and workmanship warranty (SOPREMA PLATINUM WARRANTY) is requested (warranty of the membrane manufacturer).

#### The membrane manufacturer will issue a written document in the owner’s name, valid for a [   ]-year period, stating that it will repair any leaks in the roofing membrane to restore the roofing system to a dry and watertight condition, to the extent that manufacturing or installation defects caused such water infiltration. The warranty must cover the total cost of repair(s) during the entire warranty period. The warranty must be transferable, at no extra cost, to subsequent building owners. The warranty certificate must reflect these requirements.

NOTE TO THE SPECIFIER: Retain the following article when requesting a materials warranty (warranty from the membrane manufacturer).

#### The membrane manufacturer will issue a written and signed document in the owner's name, certifying that the roofing membranes are free of manufacturing defects for a period of ten (10) years, starting from the date of completion of membrane installation. This warranty will cover the removal and replacement of defective roof membrane products, including workmanship. The warranty must remain full and complete for the duration of the period specified. The warranty certificate must reflect these requirements.

NOTE TO THE SPECIFIER: Retain the following article when requesting a workmanship warranty (warranty from the roofing contractor).

#### The contractor will provide a written and signed document to the owner’s name certifying that the work executed will remain in place and free of waterproofing defect for a [   ]-year period from the date of acceptance.

NOTE TO THE SPECIFIER: Some local roofing associations issue waterproofing warranties complementary to those previously mentioned. Please consult these local associations for the terms and conditions of these warranties.

#### [The contractor will provide [local association] a certificate of warranty for this project, valid for a [   ]-year period.]

# Products

## VAPOUR BARRIER SUPPORT PANELS

NOTE TO THE SPECIFIER: When specifying XPRESS VAP’R BOARD as “Vapour Barrier Support Panel”, use the “Vapour Barrier” Section of the specification.

### Lightweight Concrete Panel

#### Description : Non combustible lightweight concrete panel in in conformance with CAN/ULC-S114-05 « Standard Method of Test for Determination of Non-Combustibility in Building Materials ».

#### Specified product: Perma Base Dek de Unifix

### Gypsum-Fibre Roof Board

#### Description: glass fibre-covered roof board [ [ ]-mm-thick].

#### In conformance with: ASTM E84 and ASTM C1177

#### Specified product:

## VAPOUR BARRIER

NOTE TO THE SPECIFIER: Choose the vapour barrier best suited to roof substrate, and that meets possible ULC and/or FM requirements, if needed. Take into consideration humidity conditions of adjacent premises as well as general installation conditions.

### Thermal Barrier and Vapour Barrier Board

#### Description: Board of a minimum thickness of 15.8 mm (5/8 in) composed of SBS modified bitumen membrane with a polyester reinforcement, factory-laminated on a mineral wool board. The membrane measures 1 m by 4.91 m (3.28 ft x 16.10 ft). The top face is sanded. The membrane side lap is part self-adhesive and part thermofusible.

#### Specified product: XPRESS VAP’R BOARD by SOPREMA.

NOTE TO THE SPECIFIER: The vapour-barrier membrane below is self-adhesive and does not require torching or hot bitumen. However, it cannot be used under insulation board adhered with hot asphalt. Also consider application temperature limitations.

### Self-Adhesive Vapour Barrier

#### Description: Self-adhesive membrane composed of SBS modified bitumen, with a surface screen made of high-density polyethylene laminated between two layers of polyethylene films. The width of the membrane is 1.14 m (45 in) to allow the membrane to fit on the top of most structural steel deck profiles. The self-adhesive underface is protected with a silicone plastic release film.

### Modified Bitumen Vapour Barrier

#### Description: Roofing membrane composed of SBS modified bitumen and a [non-woven polyester] [glass mat] reinforcement. The upper surface is sanded, the underface is covered with a thermofusible plastic film.

#### In conformance with: CAN/CGSB 37.56-M (9th Draft).

#### Specified product: [SOPRALENE SP 3.5]  [ELASTOPHENE SP] by SOPREMA.

NOTE TO THE SPECIFIER: The vapour barrier below can be specified for buildings with low humidity levels; this type of vapour barrier can also be used with assemblies conforming to ULC and FM standards where no fire separations are required (gypsum board or other) and where certain insulations are installed directly onto steel deck. These assemblies are more economical overall.

### Kraft Paper Vapour Barrier

#### Description: [Vapour barrier composed of two layers of high moisture resistance Kraft paper bonded together with asphalt.]

#### In conformance with: ASTM E96.

#### Specified product: SOPRASTOP by SOPREMA.

NOTE TO THE SPECIFIER: Install a self-adhesive membrane strip beneath parapets and at wall junctions to ensure vapour barrier continuity, as specified below. For on-site co-ordination, this membrane must be provided by the roofer and installed by a carpenter. Specify the installation of this strip in the Carpentry Section.

### Vapour Barrier Continuity Strip

#### Description: Waterproofing membrane with composite reinforcement and SBS modified bitumen. The surface is sanded and the underface is self-adhesive and covered with a silicon release film.

#### Specified product: SOPRALENE STICK ADHESIVE by SOPREMA.

## INSULATION

### Mineral Wool Roof Insulation Board

#### Description: Mineral wool roof insulation board with a rigid surface made from basalt and steel slag.

#### Specified product: SOPRAROCK DD by SOPREMA

### Mineral Wool Roof Insulation

#### Description: Mineral wool-based roof support panel with a homogeneous density made from basalt and steel slag.

#### Specified product: SOPRAROCK MD by SOPREMA

### Polyisocyanurate Insulation

#### Description: Closed-cell polyisocyanurate foam insulation board laminated on both sides with a fiberglass yarn-reinforced organic paper.

#### Specified product: SOPRA-ISO by SOPREMA

### Tapered Insulation Board

#### Description : Tapered insulation panel made of [mineral wool] [polyisocyanurate] designed to create a [   ] percent (%) slope to the roof system.

#### Specified product : [             ]

### Sump Insulation Board for Drain Location

#### Description: Sump insulation panel made of [mineral wool] [polyisocyanurate] designed to facilitate proper drainage around drain.

#### Product specified : [             ]

## MEMBRANES

### Mineral Wool Fibre Board and Base Sheet Membrane

#### Description: Board composed of SBS modified bitumen membrane with a polyester reinforcement, factory-laminated on a mineral wool board. [The underface of wool fibre is impregnated with a layer of bitumen for applications with cold adhesives.] The membrane measures 1 m x 4.91 m (3.28 ft x 16.10 ft). The surface is [sanded] [covered with thermofusible plastic film]. The membrane side lap is part self-adhesive and part thermofusible.

#### Thickness: [    ]

#### In conformance with: CGSB 37.56-M (9th Draft).

#### Properties: 							MD 		XD

###### Strain energy (kN/m)		9	7

###### Breaking strength (kN/m)	17 	12.5

###### Ultimate elongation (%)		60 	65

###### Tear resistance (N)		60

###### Static puncture resistance (N)	400

###### Dimensional stability (%)	-0.4 	0.3

###### Plastic flow (°C)		≥ 115

###### Cold bending at -30 °C		No cracking

###### Lap joint strength (kN/m) 	Pass > 4 kN/m

#### Specified product: [XPRESS BOARD HD] [XPRESS BOARD HD SANDED] by SOPREMA

NOTE TO THE SPECIFIER: Specify a self-adhesive base sheet for flame-sensitive substrates.

### Base Sheet Membrane for Flashings and Parapets

#### Description: Membrane composed of SBS modified bitumen and [composite heavy duty] [non-woven polyester] [glass mat] reinforcement. The surface is covered with a thermofusible plastic film and the underface is [covered with a thermofusible plastic film] [covered with a release protection film]. The surface shall be marked with three (3) chalk lines to ensure proper roll alignment.

#### In conformance with: CGSB 37.56-M (9th Draft).

#### Properties: 							MD 		XD

###### Strain energy (kN/m)		[  ]	[  ]

###### Breaking strength (kN/m)	[  ] 	[  ]

###### Ultimate elongation (%)		[  ] 	[  ]

###### Tear resistance (N)		[  ]

###### Static puncture resistance (N)	[  ]

###### Dimensional stability (%)	[  ] 	[  ]

###### Plastic flow (°C)		≥ [    ]

###### Cold bending at -30 °C		No cracking

###### Lap joint strength (kN/m)	[  ]

#### Specified product: [SOPRAFLASH FLAM STICK] [SOPRALENE FLAM 180] [SOPRALENE FLAM STICK] by SOPREMA

### Board and Base Sheet Membrane for Flashings

#### Description: Board composed of SBS modified bitumen membrane with a polyester reinforcement factory-laminated to a mineral wool board. The membrane measures 1 m x 4.91 m (3.28 ft x 16.10 ft). The surface is [sanded] [covered with a thermofusible plastic film]. The membrane side lap is part self-adhesive and part thermofusible.

#### Thickness: 12.5 mm (1/2 in)

#### In conformance with: CGSB 37.56-M (9th Draft).

#### Properties: 							MD 		XD

###### Strain energy (kN/m)		9	7

###### Breaking strength (kN/m)	17 	12.5

###### Ultimate elongation (%)		60 	65

###### Tear resistance (N)		60

###### Static puncture resistance (N)	400

###### Dimensional stability (%)	-0.4 	0.3

###### Plastic flow (°C)		≥ 115

###### Cold bending at -30 °C		No cracking

###### Lap joint strength (kN/m) 	Pass > 4 kN/m

#### Specified product: [XPRESS BOARD HD] [XPRESS BOARD HD SANDED] by SOPREMA

### Colour Choices for Roofing Cap Sheet Membrane Granules

#### For field surfaces: [brown] [sienna] [red] [black] [green] [blue] [grey], [white].

#### For walkway surfaces: [brown] [sienna] [red] [black] [green] [blue] [grey], [white].

### Roofing Cap Sheet Membrane for Field Surfaces

#### Description: Roofing membrane composed of SBS modified bitumen with a composite reinforcement and elastomeric bitumen [with flame-retarding agent]. The surface is protected by coloured granules. The underface is covered with a thermofusible plastic film.

#### In conformance with: CGSB 37.56-M (9th Draft).

#### Properties: 							MD 		XD

###### Strain energy (kN/m)		7.8	7.2

###### Breaking strength (kN/m)	15 	13.5

###### Ultimate elongation (%)		60 	65

###### Tear resistance (N)		125

###### Static puncture resistance (N)	560

###### Dimensional stability (%)	0.2	0

###### Plastic flow (°C)		≥ 110

###### Cold bending at -30 °C		No cracking

###### Lap joint strength (kN/m) 	Pass > 4 kN/m

#### Specified Product: [SOPRAPLY TRAFFIC CAP 560] [SOPRAPLY TRAFFIC CAP 561] by SOPREMA

### Roofing Cap Sheet Membrane for Flashings and Parapets

#### Description: Roofing membrane composed of SBS modified bitumen with a composite reinforcement and elastomeric bitumen [with flame-retarding agent]. The surface is protected by coloured granules. The underface is covered with a thermofusible plastic film.

#### In conformance with: CGSB 37.56-M (9th Draft).

#### Properties: 							MD 		XD

###### Strain energy (kN/m)		7.8	7.2

###### Breaking strength (kN/m)	15 	13.5

###### Ultimate elongation (%)		60 	65

###### Tear resistance (N)		125

###### Static puncture resistance (N)	560

###### Dimensional stability (%)	0.2	0

###### Plastic flow (°C)		≥ 110

###### Cold bending at -30 °C		No cracking

###### Lap joint strength (kN/m) 	Pass > 4 kN/m

#### Specified Product: [SOPRAPLY TRAFFIC CAP 560] [SOPRAPLY TRAFFIC CAP 561] by SOPREMA

### Starter Roll

#### Description: Waterproofing membranes composed of SBS modified bitumen, covered with granules on surface, with a 100 mm (4 in) selvedge on both sides. The underface is covered with a thermofusible plastic film.

#### In conformance with: CGSB 37.56-M (9th Draft).

#### Properties: 							MD 		XD

###### Strain energy (kN/m)		13	10

###### Breaking strength (kN/m)	25 	21

###### Ultimate elongation (%)		66 	93

###### Tear resistance (N)		118

###### Static puncture resistance (N)	432

###### Dimensional stability (%)	-0.2 	0.2

###### Plastic flow (°C)		≥ 110

###### Cold bending at -30 °C		No cracking

###### Lap joint strength (kN/m) 	Pass > 4 kN/m

#### Specified Product: STARTER FLAM GR by SOPREMA

## ACCESSORY MEMBRANES

### Cover Strip

#### Description: Membrane strip of [330 mm (13 in)] [240 mm (9.45 in)] made of SBS modified bitumen with a composite reinforcement. Both faces are covered with a plastic thermofusible film. The strip ensures water-tightness in the end laps.

#### In conformance with: ASTM D6162.

#### Specified product: SOPRALAP by SOPREMA.

## PRIMER

### Primer for Thermofusible Membranes

#### Description: Primer made of bitumen, volatile solvents and adhesive resins. Used as primer to improve the adhesion of thermofusible waterproofing membranes.

#### Specified product: ELASTOCOL 500 by SOPREMA.

### Primer for Self-Adhesive Membranes

#### [Description: Primer composed of SBS synthetic rubber, adhesive resins and volatile solvents. Used as primer to improve the adhesion of self-adhesive membranes.]

#### Specified product: ELASTOCOL STICK by SOPREMA.

#### [Description: Primer composed of SBS synthetic rubber, adhesive resins and VOC-free solvents. Used as primer to improve the adhesion of self-adhesive membranes.

#### Specified product: ELASTOCOL STICK ZERO by SOPREMA

#### [Description: Polymeric emulsion composed of SBS synthetic rubber and adhesive resins. Used as primer to improve the adhesion of self-adhesive membranes.]

#### Specified product: ELASTOCOL STICK H20 by SOPREMA

## ADHESIVES

### Insulation Adhesive

#### Description: Two-component, quick-setting, low-expansion foam urethane adhesive that can be applied at any temperature.

#### Specified product: DUOTACK by SOPREMA

## FLAME-STOP MEMBRANE

#### Description: Self-adhesive membrane composed of SBS modified bitumen and a glass mat reinforcement, designed to prevent flames from penetrating into voids, cavities and openings before installing heat-welded membranes.

#### Specified products: SOPRAGUARD tape by SOPREMA

#### Description: Membrane composed of a reinforced glass mat coated with oxidized bitumen. Both faces are sanded.

#### Specified products: SOPRAGLASS [40] [100] by SOPREMA

## FASTENERS

### Membranes Fasteners

#### Description: [pre-assembled] fasteners with #14 self-tapping screws, with washer of 50 mm (2 in) in diameter.

#### In conformance with: FM 4470 Approvals standard.

#### Specified products: SOPRAFIX FASTENERS/PLATES by SOPREMA

### Insulation Fasteners

#### Description: [              ]

#### Specified products: [              ]

## COMPLEMENTARY WATERPROOFING PRODUCTS

NOTE TO THE SPECIFIER: Use the product described below for all sealing products in contact with the waterproofing membrane. It is recommended to cover SOPRAMASTIC with granules when it is left exposed. Aluminum pigments are added to SOPRAMASTIC ALU to provide roofing elements a greater resistance; it can be left exposed.

### Waterproofing Mastic

#### Description: Multi-purpose mastic composed of SBS modified bitumen, fibres, [aluminium pigments,] mineral fillers and solvents.

#### Specified product: SOPRAMASTIC [ALU] by SOPREMA

### Pitch Pocket Filler

#### Description: Polyester-made precast blocks of various sizes a single-component, polyether-based mastic and a single-component, polyether based sealant and adhesive.

#### Specified product: SOPRAMASTIC BLOCK SYSTEM by SOPREMA

### Sealing Product

#### Description: Bitumen/polyurethane waterproofing mono-component resin and polyester reinforcement.

#### Specified products: ALSAN FLASHING and ALSAN REINFORCEMENT by SOPREMA

## ROOF WALKWAYS

NOTE TO THE SPECIFIER: Roof walkways are meant to provide access to rooftop equipment and to protect roof membrane from any damage. Walkways can be composed of an additional layer of membrane (membrane-covered walkway), rubber mats (such as SOPRAMAT by SOPREMA), stone or concrete pavers, wood planks or of any other sufficiently rigid material compatible with the roofing membranes. An inter-layer membrane must be installed under SOPRAMAT boards.

### Membrane Walkways

#### Description: Waterproofing membrane composed of SBS modified bitumen and non-woven polyester reinforcement, used to protect membranes subjected to foot traffic. The surface is covered with black granules; the underface is protected by a thermofusible plastic film.

#### In conformance with: CGSB 37.56-M (9th Draft).

#### Specified product: SOPRAWALK by SOPREMA

#### Description: Waterproofing membrane composed of SBS modified bitumen and unwoven polyester reinforcement, used to protect membranes subjected to foot traffic. The surface is covered with red granules; the underface is protected by a thermofusible plastic film.

#### In conformance with: CGSB 37.56-M (9th Draft).

#### Specified product: SOPRASAF’T by SOPREMA

# Execution of Work

## SURFACE EXAMINATION AND PREPARATION

#### Surface examination and preparation must be completed in conformance with instructions in the membrane manufacturer’s technical documentation.

#### Before roofing work begins, the owner's representative and roofing foreman will inspect and approve deck conditions (including slopes and wood grounds) as well as flashings at parapets, roof drains, plumbing vents, ventilation outlets and other construction joints. If necessary, a non-conformity notice will be issued to the contractor so that required corrections can be carried out. The start of roofing work will be considered as acceptance of conditions for work completion.

#### Do not begin any portion of work before surfaces are clean, smooth, dry, and free of ice and debris. Use of calcium or salt is forbidden for ice or snow removal.

#### Be sure plumbing, carpentry and all other works have been duly completed.

#### No materials will be installed during rain or snowfall.

## METHOD OF EXECUTION

NOTE TO THE SPECIFIER: When demolition work is required, or when work is needed on existing materials, be sure to respect the requirements of the Workplace Hazardous Materials Information System (WHMIS). Refer to Section 01545: Safety Measures in the NMS.

NOTE TO THE SPECIFIER: Refer to membrane manufacturer for pertinent specifications (according to site conditions) when base sheet membranes remain exposed without cap sheet for more than three (3) months.

#### Roofing work must be completed in a continuous fashion as surfaces are readied and as weather conditions allows it.

#### It’s preferable to seal all joints that are not covered by a cap sheet membrane the same day. A second cap sheet cannot be installed if any moisture is present in joints.

NOTE TO THE SPECIFIER: Please retain the following clause in case of re-roofing where underlying structures must be protected.

#### Ensure waterproofing of roofs at all times, including protection during installation work by other trades and protection as work is completed (e.g. vents, drains, etc.).

## SITE PROTECTION

#### Protect the exposed surfaces of finished work to avoid damage during roof installation and material transportation. [Install walkways made of rigid boards over installed roofing materials to enable passage of people and transport of products.] Assume full responsibility for any damage.

## PREPARATION WORK – METAL DECK

#### [Install acoustic insulation in deck flutes.]

## PREPARATION WORK – CONCRETE DECK

#### Prepare surfaces according to [manufacturer’s] [local authorities’] recommendations. Surfaces to be waterproofed with elastomeric bitumen membrane must have a Concrete Surface Profile (CSP) of 3 to 6 (CSP as per the International Concrete Repair Institute).

## INSTALLATION OF VAPOUR BARRIER SUPPORT PANELS ON STEEL DECK

#### Adhere support panel using specified adhesive applied in continuous strips spaced [    ] on the field surface, [    ] on the perimeter, and [    ] on corners.

#### These boards must be screwed onto the steel deck's upper rib surfaces [at a rate of [    ] mechanical fasteners per board] [, in conformance with Factory Mutual requirements, including the PLPDS 1-29, for fastening boards at roof corners and perimeters].

#### Cut boards so edges rest on centre of upper ribs. Cut straight lines with adequate tools.

#### Where slopes change, boards will be cleanly cut (avoid breaking boards) to acquire deck shape. Place boards perpendicular to deck ribs for continuous support at extremities.

#### Board joints will be staggered, at half-length, and perfectly butted. [Joints will be sealed with heat-resistant tape in both directions to prevent any asphalt leakage in finished areas.]

## APPLICATION OF PRIMER

NOTE TO THE SPECIFIER: Please refer to Technical Data Sheets for application rate of specified products.

#### Wooden, metallic, concrete, and masonry surfaces or gypsum insulation substrate will receive a coat of primer at a rate of [    to    ] L/m2 (no primer is required for factory-painted metals). All surfaces to be primed must be free of rust, dust or any residue that may hinder adherence. Primed surfaces must be covered with the roofing membrane as soon as possible (on the same day for self-adhesive membranes).

NOTE TO THE SPECIFIER: Use the following article when a self-adhesive vapour barrier is specified. Make sure that the substrate is approved for this type of installation.

## Installation of Self-Adhesive Vapour Barrier

#### Primer must be dry prior to the installation of the vapour barrier membrane.

#### Starting at the bottom of the slope, without adhering the membrane, unroll it onto the substrate for alignment. Do not immediately remove the silicone release film.

#### Align the roll parallel to the ribs of the steel deck. Make sure membrane overlaps are supported along their entire length.

#### Remove one end of the silicone release film and adhere this part of the membrane to the substrate. Remove the remaining release film at a 45º angle to avoid wrinkles in the membrane.

#### Overlap adjacent rolls of 75 mm (3 in) and 100 mm (4 in). End laps must be 150 mm (6 in). Space end laps by at least 300 mm (12 in).

#### When the vapour barrier is installed directly on a steel deck, place a thin sheet of metal under the end laps of the vapour barrier.

## Application of Thermofusible Vapour Barrier

NOTE TO THE SPECIFIER: Ensure insulation substrate and adjoining work or construction elements pose no fire hazards during use of torch equipment. Do not weld onto old wood substrates or at locations where chimney or back draft effects could pull flames onto concealed combustible materials. Consult membrane manufacturer for alternate work methods and relevant safety guidelines.

#### Primer must be dry prior to the installation of the vapour barrier membrane.

#### Starting at the lowest point of the roof slope, the vapour barrier membrane must be heat-welded onto the substrate in conformance with manufacturer’s written recommendations.

#### Overlap adjacent rolls of 75 mm (3 in) and 100 mm (4 in). End laps must be 150 mm (6 in). Space end laps by at least 300 mm (12 in).

#### The roof vapour barrier must meet and overlap the air/vapour barrier on adjoining walls to ensure total continuity.

#### Pull up vapour barrier at insulation perimeters and around each element penetrating it to ensure sealed connections with flashing base sheet.

## Installation of Asphalted Kraft Vapour Barrier

NOTE TO THE SPECIFIER: Consult the manufacturer as needed for required instructions related to specified vapour barrier.

#### [Adhere vapour barrier to substrate with specified adhesive in conformance with manufacturer's recommendations.] [Adhere the vapour barrier to substrate and seal joints with recommended adhesive in conformance with manufacturer's recommendations.]

## Installation of Support Panel and Vapour Barrier

NOTE TO THE SPECIFIER: Use the following clause when boards are mechanically fastened to wooden or steel substrates.

#### Mechanically fasten boards with screws and plates for membranes. [Mechanical fasteners must be installed in the centre of the membrane side selvedge [and on board surface] at a rate of [    ] on the field surface, [    ] on the roof perimeter, and [    ] on corners.] [Follow instructions of approval reports for location of fasteners.]

NOTE TO THE SPECIFIER: Use the following clause when boards are installed on substrate using adhesive

#### Adhere boards by using specified adhesive in continuous strips spaced [    ] on the field surface, [    ] on the perimeter, and [    ] on corners. [Corners and perimeters must be installed as per FM requirements listed in the PLPDS 1-29].

#### Because of the nature of this system, for this type of vapour barrier, joints can be aligned (no offset) to facilitate the installation of the reinforcing strip.

#### Adhere the first part of the self-adhesive side laps using a membrane roller, then heat-weld the last part (self-adhesive, heat-welded side laps).

#### Seal the end laps by welding a 330-mm (13-in) wide protection strip centered on the joint.

## INSTALLATION OF INSULATION

NOTE TO THE SPECIFIER: Use the following clause when insulation is installed on substrate using adhesive. Check if this type of adhesive is appropriate for that type of application.

#### [Adhere insulation by using specified adhesive in continuous strips spaced [    ] on the field surface, [    ] on the perimeter, and [    ] on corners. [Corners and perimeters must be installed as per FM requirements listed in the PLPDS 1-29].

NOTE TO THE SPECIFIER: Use the following clause when boards are mechanically fastened to the substrates.

#### [Mechanically fasten boards with screws and plates for membranes, at a rate of [    ] on the field surface [, [    ] on the perimeter, and [    ] on corners]. [Corners and perimeters must be installed as per FM requirements listed in the PLPDS 1-29.] [Screws must be driven in deck's upper flutes.]]

NOTE TO THE SPECIFIER: Use the following clause when membranes and/or panels with factory-laminated membrane are mechanically fastened to the substrate.

#### [It is not required to fasten insulation boards to achieve wind uplift resistance when base sheet membranes are mechanically fastened. However, in order to prevent any insulation board movement, they can be fastened at a rate of one fastener per 4 ft2.]

NOTE TO THE SPECIFIER: Use the following clause when boards are adhered to substrate with hot asphalt.

#### [On the whole surface of the vapour barrier corresponding to the surface of the insulation block to be applied, apply a coat of hot asphalt at a rate of 1 kg/m2 (2.20 lb/ft2), according to methods and temperatures recommended by the manufacturer.]

#### All boards must be in perfect connection, without any significant variances in level, and must be completely adhered to the surface.

#### [All vertical joints between [flat boards and sloped modules] [the two rows of insulation boards] will be staggered.]

#### [Around the drain, execute a slight slope of 0 to 10 mm (0 to 0.4 in) in a 600-mm (24-in) radius.]

#### Install only as much insulation as can be covered in the same day.

## SUMP INSULATION PANEL INSTALLATION

#### Install sump insulation panel in conformance with manufacturer’s instructions and recommendations

## INSTALLATION OF FLAME-STOP MEMBRANE

NOTE TO THE SPECIFIER: Ensure insulation substrates and adjoining work or construction elements pose no hazards during use of torch equipment. Do not weld onto wood substrates or at locations where chimney or back draft effects could project flames onto concealed combustible materials. Consult membrane manufacturer for alternate work methods where such cases apply.

#### [Adhere the membrane directly onto an approved substrate by removing the silicone release film. SOPRAGUARD TAPE is designed to prevent flames from penetrating into voids, cavities and openings while installing heat-welded membranes.]

#### [Unroll the flame-stop membrane onto the insulation, being careful to overlap adjacent selvedges to ensure that the flame will not penetrate the insulation.]

## INSTALLATION OF BOARDS and FACTORY-LAMINATED BASE SHEET

NOTE TO THE SPECIFIER: Use the following clause when boards are installed on the substrate using adhesive. Check if this type of adhesive is appropriate for that type of application.

#### Adhere base sheet board using adhesive applied in continuous strips spaced 30 cm (12 in) on the field surface [, [    ] on the perimeter, and [    ] on corners. Corners and perimeters must be installed as per FM requirements listed in the PLPDS 1-29].

NOTE TO THE SPECIFIER: Use the following clause when boards are mechanically fastened to substrate.

#### Mechanically fasten boards with screws and plates for membranes. [Mechanical fasteners must be installed in the centre of the membrane side selvedge [and on board surface] at a rate of [    ] on the field surface, [    ] on the roof perimeter, and [    ] on corners.] [Follow instructions of approval reports for location of fasteners.]

#### Avoid the formation of wrinkles, swellings or fishmouths.

## INSTALLATION OF SELF-ADHESIVE BASE SHEET ON FLASHINGS AND PARAPETS

#### Apply base sheet flashing only after primer coat is dry.

#### Before applying membranes, always burn the plastic film from the section to be covered if there is an overlap (inside and outside corners and field surface). For sanded base sheet membranes, apply primer for self-adhesive membrane on the area to be covered at the foot of the parapets.

#### Cut off corners at end laps of areas to be covered by the next roll.

#### Each selvedge will overlap the previous one along lines provided for this purpose, and by 150 mm (6 in) at the ends.

#### Position the pre-cut membrane. Remove 150 mm (6 in) of the silicone release film to hold the membrane in place at the top of the parapet.

#### Then, gradually peel off the remaining silicone release film, pressing down on the membrane with an aluminum applicator to ensure good adhesion. Use the aluminum applicator to ensure a perfect transition between the flashing and the field surface. Smooth the entire membrane surface with a membrane roller for full adhesion.

#### Install a reinforcing gusset at all inside and outside corners.

#### Always seal overlaps at the end of the workday.

#### Avoid the formation of wrinkles, swellings or fishmouths.

## INSTALLATION OF WELDABLE BASE SHEET ON FLASHINGS AND PARAPETS

NOTE TO THE SPECIFIER: Ensure roofing substrates and adjoining work or construction elements pose no fire hazards during use of torch equipment. Do not torch onto wood substrates or at locations where chimney or back draft effects could project flames onto concealed combustible materials. Consult membrane manufacturer for alternate work methods where such cases apply.

#### Apply base sheet flashing only after primer coat is dry.

#### Cut off corners at end laps to be covered by the next roll.

#### Each selvedge will overlap along lines provided for this purpose, and by 150 mm (6 in) at the ends.

#### This base sheet membrane must be welded directly to the substrate, proceeding from top to bottom using a propane torch.

#### Avoid the formation of wrinkles, swellings or fishmouths.

## INSTALLATION OF REINFORCED GUSSETS

#### Install reinforcing gussets at all inside and outside corners.

#### Heat-weld the gussets in place after installing base sheet membrane.

## INSTALLATION OF WELDABLE REINFORCING MEMBRANES

#### Install reinforcing membranes specified according to the typical detailed instructions in the documentation of membrane manufacturer.

## INSTALLATION OF THERMOFUSIBLE CAP SHEET ON FIELD SURFACE

#### Begin with double-selvedge starter roll. If starter roll is not used, side laps covered with granules must be de-granulated by embedding granules in torch-heated bitumen over a 75-mm (3 in) width.

#### [Starting at drain,] Unroll the membrane on the base sheet, taking care to align the edge of the first selvedge with the edge of the roof.

#### Cut off corners at end laps at areas to be covered by the next roll.

#### Each selvedge will overlap the previous one along lines provided for this purpose, and will overlap by 150 mm (6 in) at the ends. Space end laps a minimum of 300 mm (12 in).

#### Heat-weld cap sheet membrane with a torch on the base sheet to create a bleed out of 3 to 6 mm (1/8 to 1/4 in).

#### During installation, be careful not to overheat the membrane or its reinforcements.

#### Avoid the formation of wrinkles, swellings or fishmouths.

#### Avoid walking over finished surfaces; use rigid protective walkways as needed.

## INSTALLATION OF THERMOFUSIBLE CAP SHEET ON FLASHINGS AND PARAPETS

#### This cap sheet must be installed in one-metre-wide strips  (3.25 ft).

#### Each selvedge will overlap the previous one laterally along lines provided for this purpose, and will overlap by 150 mm (6 in) the field surface. Membranes for flashings must be spaced at least 100 mm (4 in) with respect to the cap sheet membranes on the field surface, to avoid areas of excessive membrane thickness.

#### Cut off corners at end laps on areas to be covered by the next roll.

#### Use a chalk line to draw a straight line on the field surface, 150 mm (6 in) from flashings and parapets.

#### Use a torch and round-nose trowel to embed the surface granules in the layer of hot bitumen, starting from the chalk line on the field surface to the bottom edge of the flashing or parapet, as well as on the granulated vertical surfaces to be overlapped.

#### This cap sheet will be heat-welded directly to the base sheet membrane, proceeding from bottom to top.

#### Avoid the formation of wrinkles, swellings or fishmouths.

#### During installation, be careful not to overheat the membrane and its reinforcements.

## INSTALLATION OF WALKWAYS

#### Install walkways in compliance with requirements previously stipulated for cap sheet installation. Apply primer to cap sheet before installing walkways.

## WATERPROOFING FOR VARIOUS DETAILS

#### Install waterproofing membranes at various roofing details in conformance with typical details indicated in technical documentation of the manufacturer.

Note: Based on the evolution of knowledge and techniques, SOPREMA INC. may modify the composition and/or conditions of use of its products without prior notice. Consequently orders will be filled according to the latest specifications.

- END OF SECTION -