MODIFIED BITUMINOUS SHEET WATERPROOFING –

PARKING DECKS

TRAFIKROCK BASE

THIS DOCUMENT PROVIDES TECHNICAL INFORMATION REGARDING MATERIALS AND INSTALLATION METHODS FOR MODIFIED-BITUMEN SHEET WATERPROOFING COATINGS FOR PARKING DECKS AND RELATED ACCESSORIES.

FOR A COMPLETE LIST OF TECHNICAL DATA SHEETS, GUIDE SPECIFICATIONS AND DETAILS PLEASE VISIT OUR WEB SITE WWW.SOPREMA.CA

# GENERAL REQUIREMENTS

## DESCRIPTION

### Supply the labour, materials, and equipment required to complete the installation of the modified-bitumen sheet waterproofing coating system for parking decks, including surface preparation and related accessories.

### The guidelines in this document should be read in conjunction with the product data sheets.

### Modified-bitumen sheet waterproofing coating systems: TRAFIKROCK BASE by SOPREMA.

## PERFORMANCE REQUIREMENTS

### Install waterproofing system to accommodate movements of the materials and structural elements in place.

### Ensure the continuity of waterproofing materials and assemblies in accordance with the materials described in the related sections.

## REFERENCES

### ASTM D5147: Standard Test Methods for Sampling and Testing Modified Bituminous Sheet Material

### ASTM D5602: Standard Test Method for Static Puncture Resistance of Roofing Membrane Specimens

## RELATED WORK

### Division [03 00 00] [Concrete]

### Division [05 00 00] [Metal]

### Division [07 00 00] [Thermal and moisture protection]

## SUBMITTALS

### Submit manufacturers’ current product data sheets for the components of specified cold fluid-applied waterproofing membrane.

### Submit shop drawings in accordance with Section 01 33 00 – Documents/Samples to Be Submitted for Approval by the Owner, Architect, or Engineer.

## CONTRACTOR QUALIFICATIONS

### Works described in this section must be carried out by a competent contractor certified in waterproofing, employed by a company having the adequate experience and equipment necessary for the works described in this document.

## MANUFACTURER’S REPRESENTATIVE

### The waterproofing materials manufacturer may delegate a representative to visit the work site at commencement of work.

### The contractor shall at all times permit and facilitate jobsite access to any representative of the cold fluid-applied waterproofing materials manufacturer.

## MATERIALS STORAGE

### Handle materials with proper equipment.

### If the products are stored outside, cover them with an opaque protective cover after removing the covers provided at delivery.

### The delivered materials must be carefully stored and adequately protected according to the manufacturer’s recommendations in order to prevent deterioration caused by humidity, heat, direct sunlight, or any other source.

### Rolls should be stored upright, with the selvedge side positioned upward.

## QUALITY ASSURANCE AND ENVIRONMENTAL MANAGEMENT

### Supply waterproofing membrane (including the related components and accessories) from the same membrane manufacturer to ensure total system compatibility and integrity.

### The coating products manufacturer shall provide proof of ISO 9001 and ISO 14001 certifications.

## WARRANTIES

### The product manufacturer shall issue a written and signed document in the name of the owner, certifying the product will meet all the physical characteristic published by the manufacturer, for a period of 5 years, starting from the date of completion of waterproofing membrane installation. No letter amending the manufacturer’s standard warranty will be accepted and the warranty certificate must reflect these requirements.

# PRODUCTS

## BASIS OF DESIGN:

### SOPREMA CANADA, INC.

### 1688 Jean-Berchmans-Michaud

### Drummondville, QC, J2C 8E9

### Web site: www.soprema.ca

## WATERPROOFING MEMBRANES

#### A waterproofing membrane composed of non-woven polyester reinforcement and SBS modified bitumen. The top face is protected by coloured granules, the under face is covered with a thermofusible plastic film.

#### Properties:

#### Note: Choose roll size of 1 m × 200 m when specifying installation with the large automated installation equipment and 1 m × 8 m for the small automated equipment.

##### Thickness:			4.5 mm

##### Roll size: 			[1 m × 200 m] and [1 m × 8 m]

##### Tensile strength (kN/m): 	longit. (MD) = 17.0 – transv. (XD) = 11.5

##### Elongation maximum load (%): longit. (MD) = 50.0 – transv. (XD) = 65.0

##### Low temperature flexibility:	-20 °C

##### Static puncture resistance (N): 215

#### Specified product: TRAFIKROCK and TRAFIKROCK STARTER by SOPREMA.

## ACCESSORIES

### PRIMER (solvent base)

#### A blend of SBS modified bitumen, fast-evaporating solvents and adhesive enhancing additives.

#### Specified product: ANTIROCK PRIMER by SOPREMA.

[OR]

### PRIMER (bituminous emulsion)

#### A bituminous emulsion (stabilized blend of bitumen and water without solvent).

#### Specified product: ANTIROCK EMULSION PRIMER by SOPREMA.

[OR]

### PRIMER (solvent base)

#### Primer made from bitumen, fast-evaporating solvents and adhesive enhancing additives. It is required to prime most surfaces such as concrete and metal substrates in order to improve the adhesion of torch-applied waterproofing membranes

#### Specified product: ELASTOCOL 500 by SOPREMA.

### LIQUID MEMBRANE FOR FLASHING AND DETAILS

#### Waterproofing two-component polyurethane/bitumen resin [specially designed to be used in low temperature]. It is dedicated to flashings and details where it is difficult to apply waterproofing membranes.

#### Specified product: [ALSAN FLASHING] [ALSAN FLASHING WINTER] by SOPREMA.

### LIQUID MEMBRANE REINFORCEMENT

#### A flexible reinforcement made of 100 g/m² woven polyester.

#### Specified product: FLASHING REINFORCEMENT by SOPREMA.

### SEALANT

#### Black, multipurpose mastic containing SBS modified bitumen, fibres and mineral fillers. It remains flexible at low temperatures, resists flow at high temperatures, show excellent adhesion on most surfaces without primer and provides superior ageing when protection from UV radiation.

#### Specified product: ANTIROCK SEALANT by SOPREMA.

# EXECUTION

## EXAMINATION AND PREPARATION OF SURFACES

### The following conditions must be met regarding the examination and preparation of surfaces: do not begin any work until surfaces are smooth, dry, and free of ice, oil, grease, dirt, excess mortar, or other contaminants. Abrasion of the surface is required to remove contaminants. Do not use liquid products to remove contaminants. Fill in damaged surfaces so that they are as smooth as possible.

### The curing period of the concrete must be at least twenty-eight (28) days with a minimum compressive strength of 24 MPa (3,500 psi); concrete must be free of voids.

### Prepare the concrete to obtain a surface profile (ICRI CSP) of 3 or 4. Use special equipment to achieve such a profile. Shotblasting is recommended.

### The concrete substrate must have a maximum moisture content of 5% (ASTM F2659) or 1.5 kg/100 m²/24 h (ASTM F1869) or an internal relative humidity content of 75% (ASTM F2170).

### Remove release agents or other contaminants from the surface of the concrete substrate; use an approved cleaning agent, such as isopropyl alcohol, to remove them completely.

### Verify the compatibility of all membrane components with curing compounds, coatings, or other materials which are already installed on the surfaces to be treated.

### Before the work begins, the owner’s representative and the modified-bitumen sheet waterproofing coating contractor’s foreman will inspect and approve substrate condition and ensure that related work has been properly executed. If necessary, a non-conformity notice will be issued to the contractor so that required corrections can be carried out.

### Beginning the system application implies acceptance of the concrete surface as satisfactory and ready to receive the waterproofing system.

## METHOD OF EXECUTION

### Install waterproofing membranes on properly prepared and primed surfaces.

### Waterproofing work shall be performed on a continuous basis as surface and weather conditions allow.

### Adjoining surfaces shall be protected against any damage that could result from the waterproofing installation.

### Make sure to remove adhesive identification tapes on rolls of membranes.

## EQUIPMENT

### Maintain all equipment and tools in good working order.

### Note: Use the following paragraph to specify the installation of the waterproofing membrane with automated equipment for large (200 or 250 m) rolls.

### Use automated membrane installation machine, [Macaden type], that meets the following requirements:

#### Installs 1 m × 200 or 250 m rolls.

#### Self-guidance system.

#### Hot air blowers conditioning the deck surface and heat-welding the membrane.

#### Pressure rollers optimizing adherence.

#### Certified safety equipment.

### Note: Use the following paragraph to specify the installation of the waterproofing membrane with automated equipment for standard rolls.

### Use automated membrane installation machine, [Mini-Macaden type], that meets the following requirements:

#### Installs 1 m × 8 or 10 m rolls.

#### Self-guidance system.

#### Hot air blowers heat-welding the membrane.

#### Pressure roller optimizing adherence.

#### Certified safety equipment.

## PRIMER APPLICATION

### Shake the container well before application.

### Apply the primer to surfaces using a roller or a brush according to the manufacturer’s recommendations. Primed surfaces must be covered with membranes on the same day. If this is not the case, primed surfaces must be primed again.

### The primer must be dry before applying modified-bitumen sheet waterproofing membranes.

## WATERPROOFING MEMBRANE INSTALLATION

### The membrane shall be installed parallel to the longitudinal axis of the structure. The strips should preferably be unrolled in the direction of traffic. On curved surfaces of the structure, the strips should be laid out so that the angle with the axis of circulation does not exceed 60º.

### Note: The Macaden equipment allows membranes to be installed to follow curves to a maximum radius of 130 metres.

### Waterproofing membrane is installed onto the primed concrete using Macaden equipment on horizontal surfaces and using a propane torch for details, on flashing and hard-to-reach places or restricted areas.

### Waterproofing membrane shall have side laps of 75 mm (3 in) and end laps of 150 mm (6 in). Make sure that the minimum distance between end lap joints of waterproofing membranes that are overlapping of 305 mm (12 in). Prepare end laps by embedding granule surface of membrane to be overlapped (150 mm [6 in]).

### Make sure the membrane is properly welded providing a smooth application free of air pockets, fishmouths or tears. An average of 12 mm (1/2 in) of molten bitumen is required each side of the membrane.

### Finish the installation by checking all joints of the waterproofing membranes. They should be homogeneous and show no air pockets, wrinkles, or tears.

### Wrinkle repair: Degranulate the membrane around the wrinkle in all directions within a 150 mm (6 po) radius. Cut and remove the wrinkled area of the membrane. Install a membrane patch extending minimum 150 mm (6 in) beyond limits of repair area. Use trowel to treat terminations membrane.

## INSTALLATION OF LIQUID MEMBRANE FOR FLASHING AND DETAILS

### Shake the container well before application.

### Using a brush, a roller or a trowel, coat the transition at the foot of the flashing with a coat of liquid flashing membrane, applying 4 in (100 mm) horizontally and at least 4 in (100 mm) vertically above the running surface. Do not spread over more than 10 ft (3 m) of resin before placing the reinforcement.

### Proceed immediately with reinforcement for the liquid membrane, which is installed on the wet seal coat using a trowel or a brush. Repeat the operation to cover the complete surface. The liquid membrane reinforcement strips must overlap a minimum of 2 in (50 mm).

### Immediately coat the top of the reinforcement and the entire flashing or detail with a coat of liquid membrane.

### When the first coat of liquid membrane is dry (2 to 3 hours at 20 ºC room temperature), finish the waterproofing of the detail by applying a top coat over the entire surface covered by the first coat.

## SEALANT APPLICATION

### Apply sealant to the perimeters of parapets, expansion joints, perimeters of drains, and all other details once the waterproofing membrane is installed. Sealant should be installed using a trowel, an extruder or a pump.

## BASE AND/OR WEARING COURSE

### Asphalt paving is to be applied as soon as possible within 72 hours of the membrane installation. Modified bitumen membranes can withstand temporary traffic, at slow speed, of site vehicles equipped with rubber tires and the caterpillar tracks of the road-surfacing machine. Protection must be provided in areas where tracked vehicles are manoeuvring. Any other traffic requires the project manager’s approval.

### No bonding agent is required on the membrane before the application of bituminous concrete.

### Install paving asphalt at the minimum temperature of 140 °C (284 °F) at the point of contact with the membrane.

### Any cracks in the pavement after the roller has made its initial pass are indicative of a blister forming between the deck and the membrane. Immediately lance at a 45° angle using a pointed tool so that when the roller makes the next pass it will force the air trapped in the blister out and the heat from the pavement will contribute to adhere the membrane to the bridge deck.

Note: The thickness of the wearing course depends on the load and traffic that the asphalt concrete will have to withstand. Thus, the minimum thickness is 1.6 in (40 mm) after compaction for light vehicles (including areas occasionally accessible to fire vehicles and moving trucks), or 2.4 in (60 mm) after compaction for heavy vehicles. Dimensioned on a case-by-case basis when the coating is used for the traffic of special vehicles (forklifts). Variation can be accepted when using high-performance asphalt. However, a minimum thickness of 1.6 in (40 mm) must be applied.

### Minimum thickness of the bituminous mix after compaction: [40 mm (1.6 in)] [60 mm (2.4 in)].

## INSPECTION

### Inspect the entire waterproofing membrane at the end of the works before carrying on with the covering work. Any imperfections must be repaired.

## CLEANING AND PROTECTION

### The applicator shall protect the liquid-applied waterproofing system from damage during its installation. The general contractor shall make provisions to protect the liquid-applied waterproofing during the remainder of the construction period. Repair any damage that may occur after application.

### Remove protective materials after application.

### Clean and remove daily all waste and debris from the worksite to avoid damage and operation disruption.

### Clean tools with a specified cleaner.

### It is recommended to cover the installation as soon as possible.

Note: 	SOPREMA INC. reserves the right to make changes to this specification and associated details without prior notice.

- END OF SECTION -